## RMAs
RMA | RMA Date | Status | Customer | Ship To | Contact | Phone | RMA Requests in May |  | RMA Received in May |  | Not received RMAs
RMA0000217 | 2021-05-27 | Opened | AVE0002 | 0 | Remaune Jacobus | 076 763 4244 | RMA No | Count of Field1 | RMA No | Count of Field1 | RMA No | Count of Field1
RMA0000216 | 2021-05-26 | Opened | KOR0001 | 0 |  | '+64 9 916 6400 | RMA0000217 | 1 | RMA0000217 | 1 | RMA43 | 1
RMA0000215 | 2021-05-26 | Opened | IND0002 | 0 |  | '+84.4 3 9951096 | RMA0000216 | 1 | RMA0000213 | 1 | RMA45 | 1
RMA0000214 | 2021-05-25 | Opened | FIR0002 | 1 | Matthew de Woeps | 278787803 | RMA0000215 | 1 | RMA0000210 | 1 | RMA69 | 1
RMA0000213 | 2021-05-25 | Opened | CRO0002 | 4 | Kyle | 028 409 8478 | RMA0000214 | 1 | RMA0000209 | 1 | RMA126 | 1
RMA0000212 | 2021-05-21 | Opened | CEN0002 | 1 | James Hsueh |  | RMA0000213 | 1 | RMA0000207 | 1 | RMA130 | 1
RMA0000211 | 2021-05-21 | Opened | ENA0001 | 0 | Donovan Kilroe |  | RMA0000212 | 1 | RMA0000206 | 1 | RMA134 | 1
RMA0000210 | 2021-05-19 | Opened | POW0003 | 1 | Adam Kellett | '+61 04 20 707 768 | RMA0000211 | 1 | RMA0000204 | 1 | RMA159 | 1
RMA0000209 | 2021-05-19 | Opened | TLJ0001 | 0 | Andrew Clark | 03-343 4624 | RMA0000210 | 1 | RMA0000203 | 1 | RMA167 | 1
RMA0000208 | 2021-05-18 | Opened | CRO0001 | 2 | Tina Fontanini | 419-629 2220- 3955 | RMA0000209 | 1 | RMA0000202 | 1 | RMA175 | 1
RMA0000207 | 2021-05-13 | Opened | ENE0006 | 0 |  |  | RMA0000208 | 1 | RMA0000201 | 1 | RMA177 | 1
RMA0000206 | 2021-05-11 | Opened | CRO0002 | 4 | Craig Graham | 027 238 7640 | RMA0000207 | 1 | RMA0000199 | 1 | RMA182 | 1
rma0000205 | 2021-05-11 | Opened | PRO0002 | 0 | brett.taylor@profilertech.com | 03 389 2103 | RMA0000206 | 1 | RMA0000198 | 1 | RMA187 | 1
RMA0000204 | 2021-05-11 | Opened | DCP0001 | 1 | Richard Kerr | 06 359 0834 | rma0000205 | 1 | RMA0000197 | 1 | RMA189 | 1
RMA0000203 | 2021-05-10 | Opened | PRO0002 | 0 | brett.taylor@profilertech.com | 03 389 2103 | RMA0000204 | 1 | RMA0000196 | 1 | RMA200 | 1
RMA0000202 | 2021-05-10 | Opened | ENE0006 | 0 |  |  | RMA0000203 | 1 | RMA0000195 | 1 | RMA205 | 1
RMA0000201 | 2021-05-10 | Opened | CRO0002 | 4 | Kyle | 028 4098474 | RMA0000202 | 1 | RMA0000194 | 1 | RMA208 | 1
RMA0000200 | 2021-05-04 | Opened | CRO0001 | 2 | Tina Fontanini | 419-629 2220- 3955 | RMA0000201 | 1 | RMA0000193 | 1 | RMA211 | 1
RMA0000199 | 2021-05-03 | Opened | PRO0002 | 0 | brett.taylor@profilertech.com | 03 389 2103 | RMA0000200 | 1 | RMA0000192 | 1 | RMA212 | 1
RMA0000198 | 2021-05-03 | Opened | KOR0001 | 3 | Alistair Powell | 21442966 | RMA0000199 | 1 | RMA0000191 | 1 | RMA214 | 1
RMA0000197 | 2021-05-03 | Opened | PRO0002 | 0 | brett.taylor@profilertech.com | 03 389 2103 | RMA0000198 | 1 | RMA0000188 | 1 | RMA215 | 1
RMA0000196 | 2021-04-29 | Opened | ENE0006 | 0 |  |  | RMA0000197 | 1 | RMA0000185 | 1 | RMA216 | 1
RMA0000195 | 2021-04-28 | Opened | PRO0002 | 0 | brett.taylor@profilertech.com | 03 389 2103 | RMA0000196 | 1 | RMA0000184 | 1 | Grand Total | 21
RMA0000194 | 2021-04-28 | Opened | TEA0001 | 1 | Nizar Jaber | '+64 21 197 2465 | RMA0000195 | 1 | RMA0000181 | 1
RMA0000193 | 2021-04-28 | Opened | TEA0001 | 1 | Nizar Jaber | '+64 21 197 2465 | RMA0000194 | 1 | rma0000090 | 1
RMA0000192 | 2021-04-28 | Opened | CRO0002 | 4 |  | '+64 9 274 4069 | RMA0000193 | 1 | Grand Total | 24
[7 empty] | RMA0000192 | 1
[7 empty] | Grand Total | 26 | [5 empty] | April | May
[13 empty] | RMA Request | 19 | 26
[13 empty] | RMA Received | 14 | 24
[13 empty] | Not received RMA | 18 | 21

## Line items
RMA | Name | RMA Date | RMA Line | Item | Description | Cust Item | Qty To Return | RMA Line Status | Return | Warranty | Last Return | Reason | Report Item | Cust RMA | Wty Confirmed | EnatelWarrantyVoidReasonGridCol Wty Void Reason | Serial Number | Tech Name | Tech Date | Technical Analysis | Root Cause | Known Failure Mode | Component Ref | Disposition
RMA0000217 | Averge Technologies (Pty) Ptd | 2021-05-27 | 1 | PSC14070561-031 | 5U Compact, -48, 7R, 14kW, Telkom200 | AD500231 | 1 | Filled | 1 | 1 | 2021-05-28 | Missing AC connector insulation cover | PSC14070561-031 |  | Yes |  | 2104015188 | Neal.Peng | 2021-05-27 | P/N of the missing cover: ENP-IN080120-01 | Missing Component |  | AC connector insulation cover | Replacement is in FGs, ready to go to customer.
RMA0000217 | Averge Technologies (Pty) Ptd | 2021-05-27 | 2 | PSC14070561-031 | 5U Compact, -48, 7R, 14kW, Telkom200 | AD500231 | 1 | Filled | 1 | 1 | 2021-05-28 | Missing AC connector insulation cover | PSC14070561-031 |  | Yes |  | 2104015189 | Neal.Peng | 2021-05-27 | P/N of the missing cover: ENP-IN080120-01 | Missing Component |  | AC connector insulation cover | Replacement is in FGs, ready to go to customer.
RMA0000217 | Averge Technologies (Pty) Ptd | 2021-05-27 | 3 | PSC14070561-031 | 5U Compact, -48, 7R, 14kW, Telkom200 | AD500231 | 1 | Filled | 1 | 1 | 2021-05-28 | Missing AC connector insulation cover | PSC14070561-031 |  | Yes |  | 2104015190 | Neal.Peng | 2021-05-27 | P/N of the missing cover: ENP-IN080120-01 | Missing Component |  | AC connector insulation cover | Replacement is in FGs, ready to go to customer.
RMA0000217 | Averge Technologies (Pty) Ptd | 2021-05-27 | 4 | PSC14070561-031 | 5U Compact, -48, 7R, 14kW, Telkom200 | AD500231 | 1 | Filled | 1 | 1 | 2021-05-28 | Missing AC connector insulation cover | PSC14070561-031 |  | Yes |  | 2104015191 | Neal.Peng | 2021-05-27 | P/N of the missing cover: ENP-IN080120-01 | Missing Component |  | AC connector insulation cover | Replacement is in FGs, ready to go to customer.
RMA0000217 | Averge Technologies (Pty) Ptd | 2021-05-27 | 5 | PSC14070561-031 | 5U Compact, -48, 7R, 14kW, Telkom200 | AD500231 | 1 | Filled | 1 | 1 | 2021-05-28 | Missing AC connector insulation cover | PSC14070561-031 |  | Yes |  | 2104015192 | Neal.Peng | 2021-05-27 | P/N of the missing cover: ENP-IN080120-01 | Missing Component |  | AC connector insulation cover | Replacement is in FGs, ready to go to customer.
RMA0000217 | Averge Technologies (Pty) Ptd | 2021-05-27 | 6 | PSC14070561-031 | 5U Compact, -48, 7R, 14kW, Telkom200 | AD500231 | 1 | Filled | 1 | 1 | 2021-05-28 | Missing AC connector insulation cover | PSC14070561-031 |  | Yes |  | 2104015193 | Neal.Peng | 2021-05-27 | P/N of the missing cover: ENP-IN080120-01 | Missing Component |  | AC connector insulation cover | Replacement is in FGs, ready to go to customer.
RMA0000217 | Averge Technologies (Pty) Ptd | 2021-05-27 | 7 | PSC14070561-031 | 5U Compact, -48, 7R, 14kW, Telkom200 | AD500231 | 1 | Filled | 1 | 1 | 2021-05-28 | Missing AC connector insulation cover | PSC14070561-031 |  | Yes |  | 2104015194 | Neal.Peng | 2021-05-27 | P/N of the missing cover: ENP-IN080120-01 | Missing Component |  | AC connector insulation cover | Replacement is in FGs, ready to go to customer.
RMA0000217 | Averge Technologies (Pty) Ptd | 2021-05-27 | 8 | PSC14070561-031 | 5U Compact, -48, 7R, 14kW, Telkom200 | AD500231 | 1 | Filled | 1 | 1 | 2021-05-28 | Missing AC connector insulation cover | PSC14070561-031 |  | Yes |  | 2104015195 | Neal.Peng | 2021-05-27 | P/N of the missing cover: ENP-IN080120-01 | Missing Component |  | AC connector insulation cover | Replacement is in FGs, ready to go to customer.
RMA0000217 | Averge Technologies (Pty) Ptd | 2021-05-27 | 9 | PSC14070561-031 | 5U Compact, -48, 7R, 14kW, Telkom200 | AD500231 | 1 | Filled | 1 | 1 | 2021-05-28 | Missing AC connector insulation cover | PSC14070561-031 |  | Yes |  | 2104015213 | Neal.Peng | 2021-05-27 | P/N of the missing cover: ENP-IN080120-01 | Missing Component |  | AC connector insulation cover | Replacement is in FGs, ready to go to customer.
RMA0000210 | Powerbox Australia PTY LTD | 2021-05-19 | 1 | SM1848HE-06 | 1.8kW 48V LV HE Solar Converter Module |  | 1 | Filled | 1 | 1 | 2021-05-26 | Module not recognised when installed. | SM1848HE-06 |  | No | No Fault Found | 2101010173 | Neal.Peng | 2021-05-27 | First test on bench, turned on by 130Vdc from PSU, Checked good via bench PSU, product ID(??) read correct, 62D2. O/p voltage 54V. See note. | No Fault Found |  |  | Might need Sales Eng to go back to customer first.
rma0000090 | Vital Ltd | 2020-10-29 | 1 | MRPITEMEE | P-CM624/48 |  | 1 | Filled | 1 | 0 | 2021-05-25 | DC/DC converters fan fail alarm on | P-CM624/48 |  | No | NA | 1844340259 | Neal.Peng | 2021-05-25 | All FETs and diodes were checked good. Found Glue on T300 and PCB under T300 burnt out. Fan not ran on jig. Suspect fan got faulty which caused output choke to be overheated and preloader worked incorrectly then burnt PCB. | Faulty Component |  | Fan, PCB | Unit is BER and out of warranty. Need confirm with customer if they want it back.
rma0000090 | Vital Ltd | 2020-10-29 | 2 | MRPITEMEE | P-CM624/48 |  | 1 | Filled | 1 | 0 | 2021-05-25 | DC/DC converters fan fail alarm on | P-CM624/48 |  | No | NA | 1823259916 | Neal.Peng | 2021-05-25 | All FETs and diodes were checked good. Found Glue on T300 and PCB under T300 burnt out. Fan not ran on jig. Suspect fan got faulty which caused output choke to be overheated and preloader worked incorrectly then burnt PCB. | Faulty Component |  | Fan, PCB | Unit is BER and out of warranty. Need confirm with customer if they want it back.
RMA0000207 | Enetek Power Group PTE Ltd | 2021-05-13 | 1 | MRPITEMEE | P-RW624U-21 |  | 1 | Filled | 1 | 0 | 2021-05-19 | Not working | P-RW624U-21 |  | No |  | 1723094800 | Neal.Peng | 2021-05-19 | All FETs and diodes were checked good. Turned it on with AC, only got 24.5V float volage and it's unstable, adjusted trimpot VR205 and o/p voltage jumped to normal value 27.2V See note. | Faulty Component |  | Trimpots | Serviced and ready to go back to customer.
RMA0000209 | TLJ Switchgear Ltd. | 2021-05-19 | 1 | RM1524HE-08 | 1.5kW 24V HE Rectifier Module |  | 1 | Filled | 1 | 1 | 2021-05-19 | Damaged prior to shipping. | RM1524HE-08 |  | Yes |  | 2102004062 | Neal.Peng | 2021-05-19 | Out of box failure, unit been dropped prior to shipping. | Damaged Component |  | Rear cornoer of chassis. | BER. Replacement has been sent to customer under C0991. S/N 2102004047
RMA0000204 | DC Power Ltd | 2021-05-11 | 1 | MRPITEMMP | P-BMMU-ECO-00 |  | 1 | Filled | 1 | 1 | 2021-05-13 | The BMM freezes and we can't log in, will say no comms and we can'tcommunicate with the device. | P-BMMU-ECO-00 |  | NA |  | 2005650617
RMA0000188 | Enetek Power Group PTE Ltd | 2021-04-21 | 1 | MRPITEMEE | P-RM3048HE-08T |  | 1 | Filled | 1 | 1 | 2021-05-11 | module fan failsystem installed at rooftop, under the IP66 rated cabinet | P-RM3048HE-08T |  | No | Adverse environment | 1904437194 | Neal.Peng | 2021-05-11 | Dusty on fan and area behand fan. Input fuses, boost FETs, primary FETs and secondary FETs were check good. Aux rails and w/fs checked good on bench. Got short circuit when tested fan on jig, fan died. New fan worked good on unit. See note. | Environmental & Contamination |  | Fan | Serviced and ready to go back to customer.
RMA0000191 | Averge Technologies (Pty) Ptd | 2021-04-27 | 1 | PSC14070561-031 | 5U Compact, -48, 7R, 14kW, Telkom200 | AD500231 | 1 | Filled | 1 | 1 | 2021-05-11 | Received without C/Breaker trip-protect cover. | PSC14070561-031 |  | Yes |  | 2103010254 | Neal.Peng | 2021-04-29 | Missing C/Breaker trip-protect cover. System is not actually returned. We only send the replacement. | Missing Component |  |  | Replacement is ready to go to customer.
RMA0000191 | Averge Technologies (Pty) Ptd | 2021-04-27 | 2 | PSC14070561-031 | 5U Compact, -48, 7R, 14kW, Telkom200 | AD500231 | 1 | Filled | 1 | 1 | 2021-05-11 | Received without C/Breaker trip-protect cover. | PSC14070561-031 |  | Yes |  | 2103010260 | Neal.Peng | 2021-04-29 | Missing C/Breaker trip-protect cover. System is not actually returned. We only send the replacement. | Missing Component |  |  | Replacement is ready to go to customer.
RMA0000191 | Averge Technologies (Pty) Ptd | 2021-04-27 | 3 | PSC14070561-031 | 5U Compact, -48, 7R, 14kW, Telkom200 | AD500231 | 1 | Filled | 1 | 1 | 2021-05-11 | Received without C/Breaker trip-protect cover. | PSC14070561-031 |  | Yes |  | 2103010281 | Neal.Peng | 2021-04-29 | Missing C/Breaker trip-protect cover. System is not actually returned. We only send the replacement. | Missing Component |  |  | Replacement is ready to go to customer.
RMA0000191 | Averge Technologies (Pty) Ptd | 2021-04-27 | 4 | PSC14070561-031 | 5U Compact, -48, 7R, 14kW, Telkom200 | AD500231 | 1 | Filled | 1 | 1 | 2021-05-11 | Received without C/Breaker trip-protect cover. | PSC14070561-031 |  | Yes |  | 2012006863 | Neal.Peng | 2021-04-29 | Missing C/Breaker trip-protect cover. System is not actually returned. We only send the replacement. | Missing Component |  |  | Replacement is ready to go to customer.
RMA0000191 | Averge Technologies (Pty) Ptd | 2021-04-27 | 5 | PSC14070561-031 | 5U Compact, -48, 7R, 14kW, Telkom200 | AD500231 | 1 | Filled | 1 | 1 | 2021-05-11 | Received without C/Breaker trip-protect cover. | PSC14070561-031 |  | Yes |  | 2103010253 | Neal.Peng | 2021-04-29 | Missing C/Breaker trip-protect cover. System is not actually returned. We only send the replacement. | Missing Component |  |  | Replacement is ready to go to customer.
RMA0000191 | Averge Technologies (Pty) Ptd | 2021-04-27 | 6 | PSC14070561-031 | 5U Compact, -48, 7R, 14kW, Telkom200 | AD500231 | 1 | Filled | 1 | 1 | 2021-05-11 | Received without C/Breaker trip-protect cover. | PSC14070561-031 |  | Yes |  | 2012006846 | Neal.Peng | 2021-04-29 | Missing C/Breaker trip-protect cover. System is not actually returned. We only send the replacement. | Missing Component |  |  | Replacement is ready to go to customer.
RMA0000191 | Averge Technologies (Pty) Ptd | 2021-04-27 | 7 | PSC14070561-031 | 5U Compact, -48, 7R, 14kW, Telkom200 | AD500231 | 1 | Filled | 1 | 1 | 2021-05-11 | Received without back plain cover. | PSC14070561-031 |  | Yes |  | 2103010247 | Neal.Peng | 2021-04-29 | Missing back plain cover. System is not actually returned. We only send the replacement. | Missing Component |  |  | Replacement is ready to go to customer.
RMA0000191 | Averge Technologies (Pty) Ptd | 2021-04-27 | 8 | PSC14070561-031 | 5U Compact, -48, 7R, 14kW, Telkom200 | AD500231 | 1 | Filled | 1 | 1 | 2021-05-11 | Received without back plain cover. | PSC14070561-031 |  | Yes |  | 2103010269 | Neal.Peng | 2021-04-29 | Missing back plain cover. System is not actually returned. We only send the replacement. | Missing Component |  |  | Replacement is ready to go to customer.
RMA0000191 | Averge Technologies (Pty) Ptd | 2021-04-27 | 9 | PSC14070561-031 | 5U Compact, -48, 7R, 14kW, Telkom200 | AD500231 | 1 | Filled | 1 | 1 | 2021-05-11 | Received without back plain cover. | PSC14070561-031 |  | Yes |  | 2103010256 | Neal.Peng | 2021-04-29 | Missing back plain cover. System is not actually returned. We only send the replacement. | Missing Component |  |  | Replacement is ready to go to customer.
RMA0000196 | Enetek Power Group PTE Ltd | 2021-04-29 | 1 | MRPITEMEE | P-RM3048HE-08T |  | 1 | Filled | 1 | 1 | 2021-05-11 | No output | P-RM3048HE-08T |  | No | Adverse environment | 1903409808 | Neal.Peng | 2021-05-11 | Unit is very dirty on fan and area behind fan, corrosion could be found on fan, cover, screw, PCB and some parts. Input fuses, boost FETs, primary FETs and secondary FETs were checked good. Fan not working on jig. See note. | Environmental & Contamination |  | Fan, aux circuitry | BER and warranty is voided due to corrosion. Customer confirmed to dispose it at Enatel.
RMA0000184 | CPS National Pty Ltd - Attn: Greg Campbell | 2021-04-19 | 1 | MEC-SHC1U400-06 | 1U 4 Across 1kW DC/DC Shelf V6 |  | 1 | Filled | 1 | 1 | 2021-05-10 | Converter in Vodafone Trial site went faulty. Swapped it to other positions but this made no difference. Murray Wyma is across the issue.All 3 modules failed and would be returned. | MEC-SHC1U400-06 |  | NA |  | 2006671190 | Neal.Peng | 2021-05-11 | Passed System test, done by Eric Chen.
RMA0000184 | CPS National Pty Ltd - Attn: Greg Campbell | 2021-04-19 | 2 | CM1860-48-15 | DC-DC converter 1.8KW 60/48 |  | 1 | Filled | 1 | 1 | 2021-05-10 | Converter in Vodafone Trial site went faulty. Swapped it to other positions but this made no difference. Murray Wyma is across the issue. | CM1860-48-15 |  | NA |  | 2008017214 | Neal.Peng | 2021-05-11 | Vop58.08V, Vnoise30mV@25A, IL31A, OVSD59.9V. Current hold at 32.6A. Passed BI.
RMA0000184 | CPS National Pty Ltd - Attn: Greg Campbell | 2021-04-19 | 3 | CM1860-48-15 | DC-DC converter 1.8KW 60/48 |  | 1 | Filled | 1 | 1 | 2021-05-10 | Converter in Vodafone Trial site went faulty. Swapped it to other positions but this made no difference. Murray Wyma is across the issue.All 3 modules failed and would be returned. | CM1860-48-15 |  | NA |  | 2008017250 | Neal.Peng | 2021-05-11 | Vop56.8V, Vnoise25mV@25A, IL31A, OVSD59.8V. Current hold at 33.6A. Passed BI.
RMA0000184 | CPS National Pty Ltd - Attn: Greg Campbell | 2021-04-19 | 4 | CM1860-48-15 | DC-DC converter 1.8KW 60/48 |  | 1 | Filled | 1 | 1 | 2021-05-10 | Converter in Vodafone Trial site went faulty. Swapped it to other positions but this made no difference. Murray Wyma is across the issue.All 3 modules failed and would be returned. | CM1860-48-15 |  | NA |  | 2008017238 | Neal.Peng | 2021-05-11 | Vop58.01V, Vnoise25mV@25A, IL30.2A, OVSD59.9V. Current hold at 32.7A. Passed BI.
RMA0000198 | Kordia/FENZ | 2021-05-03 | 1 | PSC24V2-403-001 | 2U +12V/24V, 2R 2C, 11+1L, 3B, EM4x |  | 1 | Filled | 1 | 1 | 2021-05-04 | On start up it goes straight to the Alarm screen. The enter button on the front panel seems to have no function and when exiting to the Enatel Splash screen it immediately jumps to whatever is selected on the Overview screen (default selection is Alarms, hence starting on the alarm screen)S/N of returned Monitor: 2008014656 | PSC24V2-403-001 |  | Yes | NA | 2011005726 | Neal.Peng | 2021-05-04 | Enter button not working. Buttons worked fine on ref unit. Used a ref Linux card on the RMA unit, fault disappear. Tested returned Linux card on ATE and it failed. Looks like IC1 on Linux card got faulty. See note. | Faulty Component |  | IC1 | Serviced and ready to go to customer.
RMA0000193 | Vital Limited | 2021-04-28 | 1 | MRPITEMEE | P-SM36-NT2-01 |  | 1 | Filled | 1 | 0 | 2021-05-03 | Fault: Connected single wire bus management on J12 between ultra and 12/24V expansion and the rectifiers blew up | P-SM36-NT2-01 |  | No | No Fault Found | 1902401132 | Neal.Peng | 2021-05-04 | NFF on this monitor. Customer incorrectly connected the rectifiers shelf and the converter shelf, and caused 2x RM2048HEs blew up. | No Fault Found |  |  | Unit is ready to go back to customer.
RMA0000193 | Vital Limited | 2021-04-28 | 2 | MRPITEMEE | P-RM2048HE-12 |  | 1 | Filled | 1 | 0 | 2021-05-03 | Fault: Connected single wire bus management on J12 between ultra and 12/24V expansion and the rectifiers blew up | P-RM2048HE-12 |  | No | Customer electrical damage | 1902395189 | Neal.Peng | 2021-05-04 | Main stage FETs Q115/Q117 failed short, no comms due to PCB fuse for comms burnt out. Root cause suspect incorrect connection by customer shorted the SBI rail and damaged Micro, therefore main stage failed. | Incorrect Customer set-up/operation |  | Q115, Q117, PCB fuse, Micro | Unit is BER and out of warranty. Customer requested it back.
RMA0000193 | Vital Limited | 2021-04-28 | 3 | MRPITEMEE | P-RM2048HE-12 |  | 1 | Filled | 1 | 0 | 2021-05-03 | Fault: Connected single wire bus management on J12 between ultra and 12/24V expansion and the rectifiers blew up | P-RM2048HE-12 |  | No | Customer electrical damage | 1902394760 | Neal.Peng | 2021-05-04 | Main stage FETs Q115/Q117 failed short, no comms due to PCB fuse for comms burnt out. Root cause suspect incorrect connection by customer shorted the SBI rail and damaged Micro, therefore main stage failed. | Incorrect Customer set-up/operation |  | Q115, Q117, PCB fuse, Micro | Unit is BER and out of warranty. Customer requested it back.
RMA0000193 | Vital Limited | 2021-04-28 | 4 | MRPITEMEE | PSC04020160-001 |  | 1 | Filled | 1 | 0 | 2021-05-03 | Fault: Connected single wire bus management on J12 between ultra and 12/24V expansion and the rectifiers blew up | PSC04020160-001 |  | No | No Fault Found | 1903404770 | Neal.Peng | 2021-05-03 | NFF on this shelf. Customer incorrectly connected the rectifiers shelf and the converter shelf, and caused 2x RM2048HEs blew up. | No Fault Found |  |  | Unit is ready to go back to customer.
RMA0000181 | Indochina Technology JSC | 2021-04-15 | 1 | RM848HE-08 | 860W 48V HE Rectifier Module |  | 1 | Filled | 1 | 1 | 2021-04-29 | Faultly | RM848HE-08 |  | Yes | NA | 2008011556 | Neal.Peng | 2021-04-29 | Input fuses opened. C110 blown up due to voltage withstand not large enough for mains swells. this is an known issue in old version. First unit failed due to this issue in version 08. Diode bridge, boost stage all checked good. | Known Failure Mode | RM848HE-05 C110 failed. C121 & C122 arcing | C110 | BER due to damaged PCB. Replacement is needed.
RMA0000185 | Indochina Technology JSC | 2021-04-19 | 1 | RM2048XE-38 | 2kW 48V Rectifier Module |  | 1 | Filled | 1 | 1 | 2021-04-29 | Fan fail anh faulty | RM2048XE-38 |  | Yes |  | 2009008088 | Neal.Peng | 2021-05-03 | Input fuses, diode bridge, boost FETs and main FETs were checked good. R634/R634A burnt out. Fan not worked on jig. Considering its age, suspect root cause is unknown voltage swell on secondary aux rail killed fan and fan drive. | Damaged Component |  | Q195 Fan R634 R634A | Unit has been serviced and ready to go to customer.
RMA0000185 | Indochina Technology JSC | 2021-04-19 | 2 | RM2048XE-38 | 2kW 48V Rectifier Module |  | 1 | Filled | 1 | 1 | 2021-04-29 | Fan fail anh faulty | RM2048XE-38 |  | Yes |  | 2008018372 | Neal.Peng | 2021-05-03 | Input shunts blew up, all main stage FETs failed, R634/R634A burnt out, fan not ran on jig. Pad got damaged due to blown up. See note. | Damaged Component |  | Q195 Fan R634 R634A Q184 Q185 Q186 Q187 R21A R22A | Unit is BER due to damaged PCB, in warranty. Need replacement to be sent to customer.
RMA0000185 | Indochina Technology JSC | 2021-04-19 | 3 | RM2048XE-38 | 2kW 48V Rectifier Module |  | 1 | Filled | 1 | 1 | 2021-04-29 | Fan fail anh faulty | RM2048XE-38 |  | Yes |  | 2008018137 | Neal.Peng | 2021-05-03 | Input fuses, diode bridge, boost FETs and main FETs were checked good. R634/R634A burnt out. Fan not worked on jig. Considering its age, suspect root cause is unknown voltage swell on secondary aux rail killed fan and fan drive. | Damaged Component |  | Q195 Fan R634 R634A | Unit has been serviced and ready to go to customer.
RMA0000194 | Vital Limited | 2021-04-28 | 1 | CM612-48-08 | 600W 12V DC:DC Converter Module |  | 1 | Filled | 1 | 1 | 2021-04-29 | Rectifier LED alarm indications, could not successfully connect monitoring bus to see the exact alarm as the rectifier blew up. Out-of-box failure. | CM612-48-08 |  | Yes | NA | 2010015262 | Neal.Peng | 2021-04-29 | No evidence of blown up, good measurement on all critical parts. Turned unit on with bench supply, found yellow led lit on all the time without any alarm activated. Solder short across P600 and P601. Removed and fault cleared. | Solder Short |  | Yellow LED | Unit has been serviced and ready to go to customer.
Finished RMAs in May
RMA No | Quantity of investigated items | Quantity of serviced items | Quantity of BER
RMA0000217 | 9 | 9 | 0
RMA0000210 | 1 | 1 | 0
RMA0000090 | 2 | 0 | 2
RMA0000207 | 1 | 1 | 0
RMA0000209 | 1 | 1 | 0
RMA0000204 | 1 | 0 | 0
RMA0000188 | 1 | 1 | 0
RMA0000191 | 9 | 9 | 0
RMA0000196 | 1 | 0 | 1
RMA0000184 | 4 | 0 | 0
RMA0000198 | 1 | 1 | 0
RMA0000193 | 4 | 2 | 2
RMA0000194 | 1 | 1 | 0
RMA0000181 | 1 | 0 | 1
RMA0000185 | 3 | 2 | 1
Grand Total | 40 | 28 | 7
Warranty
RMA No | In warratny quantity | Out of warranty quantity | Warranty void
RMA0000217 | 9 | 0 | 0
RMA0000210 | 1 | 0 | 1
RMA0000090 | 0 | 2 | 0
RMA0000207 | 0 | 1 | 0
RMA0000209 | 1 | 0 | 0
RMA0000204 | 1 | 0 | 0
RMA0000188 | 1 | 0 | 1
RMA0000191 | 9 | 0 | 0
RMA0000196 | 1 | 0 | 1
RMA0000184 | 4 | 0 | 0
RMA0000198 | 1 | 0 | 0
RMA0000193 | 0 | 4 | 0
RMA0000194 | 1 | 0 | 0
RMA0000181 | 1 | 0 | 0
RMA0000185 | 3 | 0 | 0
Grand Total | 33 | 7 | 3

## Line items - Crown
RMA | Name | RMA Date | RMA Line | Item | Description | Cust Item | Qty To Return | RMA Line Status | Return | Warranty | Last Return | Reason | Report Item | Cust RMA | Wty Confirmed | EnatelWarrantyVoidReasonGridCol Wty Void Reason | Serial Number | Tech Name | Tech Date | Technical Analysis | Root Cause | Known Failure Mode | Component Ref | Disposition
RMA0000217 | Averge Technologies (Pty) Ptd | 2021-05-27 | 1 | PSC14070561-031 | 5U Compact, -48, 7R, 14kW, Telkom200 | AD500231 | 1 | Filled | 1 | 1 | 2021-05-28 | Missing AC connector insulation cover | PSC14070561-031 |  | Yes |  | 2104015188 | Neal.Peng | 2021-05-27 | P/N of the missing cover: ENP-IN080120-01 | Missing Component |  | AC connector insulation cover | Replacement is in FGs, ready to go to customer.
RMA0000217 | Averge Technologies (Pty) Ptd | 2021-05-27 | 2 | PSC14070561-031 | 5U Compact, -48, 7R, 14kW, Telkom200 | AD500231 | 1 | Filled | 1 | 1 | 2021-05-28 | Missing AC connector insulation cover | PSC14070561-031 |  | Yes |  | 2104015189 | Neal.Peng | 2021-05-27 | P/N of the missing cover: ENP-IN080120-01 | Missing Component |  | AC connector insulation cover | Replacement is in FGs, ready to go to customer.
RMA0000217 | Averge Technologies (Pty) Ptd | 2021-05-27 | 3 | PSC14070561-031 | 5U Compact, -48, 7R, 14kW, Telkom200 | AD500231 | 1 | Filled | 1 | 1 | 2021-05-28 | Missing AC connector insulation cover | PSC14070561-031 |  | Yes |  | 2104015190 | Neal.Peng | 2021-05-27 | P/N of the missing cover: ENP-IN080120-01 | Missing Component |  | AC connector insulation cover | Replacement is in FGs, ready to go to customer.
RMA0000217 | Averge Technologies (Pty) Ptd | 2021-05-27 | 4 | PSC14070561-031 | 5U Compact, -48, 7R, 14kW, Telkom200 | AD500231 | 1 | Filled | 1 | 1 | 2021-05-28 | Missing AC connector insulation cover | PSC14070561-031 |  | Yes |  | 2104015191 | Neal.Peng | 2021-05-27 | P/N of the missing cover: ENP-IN080120-01 | Missing Component |  | AC connector insulation cover | Replacement is in FGs, ready to go to customer.
RMA0000217 | Averge Technologies (Pty) Ptd | 2021-05-27 | 5 | PSC14070561-031 | 5U Compact, -48, 7R, 14kW, Telkom200 | AD500231 | 1 | Filled | 1 | 1 | 2021-05-28 | Missing AC connector insulation cover | PSC14070561-031 |  | Yes |  | 2104015192 | Neal.Peng | 2021-05-27 | P/N of the missing cover: ENP-IN080120-01 | Missing Component |  | AC connector insulation cover | Replacement is in FGs, ready to go to customer.
RMA0000217 | Averge Technologies (Pty) Ptd | 2021-05-27 | 6 | PSC14070561-031 | 5U Compact, -48, 7R, 14kW, Telkom200 | AD500231 | 1 | Filled | 1 | 1 | 2021-05-28 | Missing AC connector insulation cover | PSC14070561-031 |  | Yes |  | 2104015193 | Neal.Peng | 2021-05-27 | P/N of the missing cover: ENP-IN080120-01 | Missing Component |  | AC connector insulation cover | Replacement is in FGs, ready to go to customer.
RMA0000217 | Averge Technologies (Pty) Ptd | 2021-05-27 | 7 | PSC14070561-031 | 5U Compact, -48, 7R, 14kW, Telkom200 | AD500231 | 1 | Filled | 1 | 1 | 2021-05-28 | Missing AC connector insulation cover | PSC14070561-031 |  | Yes |  | 2104015194 | Neal.Peng | 2021-05-27 | P/N of the missing cover: ENP-IN080120-01 | Missing Component |  | AC connector insulation cover | Replacement is in FGs, ready to go to customer.
RMA0000217 | Averge Technologies (Pty) Ptd | 2021-05-27 | 8 | PSC14070561-031 | 5U Compact, -48, 7R, 14kW, Telkom200 | AD500231 | 1 | Filled | 1 | 1 | 2021-05-28 | Missing AC connector insulation cover | PSC14070561-031 |  | Yes |  | 2104015195 | Neal.Peng | 2021-05-27 | P/N of the missing cover: ENP-IN080120-01 | Missing Component |  | AC connector insulation cover | Replacement is in FGs, ready to go to customer.
RMA0000217 | Averge Technologies (Pty) Ptd | 2021-05-27 | 9 | PSC14070561-031 | 5U Compact, -48, 7R, 14kW, Telkom200 | AD500231 | 1 | Filled | 1 | 1 | 2021-05-28 | Missing AC connector insulation cover | PSC14070561-031 |  | Yes |  | 2104015213 | Neal.Peng | 2021-05-27 | P/N of the missing cover: ENP-IN080120-01 | Missing Component |  | AC connector insulation cover | Replacement is in FGs, ready to go to customer.
RMA0000213 | Crown Equipment Limited | 2021-05-25 | 1 | MRPITEMMP | FS3LNV-530-NZ01 |  | 1 | Filled | 1 | 0 | 2021-05-26 | Failed.Send report for repairneil.thurlow@crown.com | FS3LNV-530-NZ01 |  | NA |  | 1606884290 | Jason.Liu | 2021-05-26 | Unit is badly damaged by impact, top lid handle damaged , lid deformed, upperside of the chasis is dented to the point that the front panel PCB was hit and snapped and components detached from the PCB board | Customer Damage |  |  | Unit is BER, write off, No charge PO#46681 , will issue them a report. Invoice Crown NZ attention Kyle.
RMA0000210 | Powerbox Australia PTY LTD | 2021-05-19 | 1 | SM1848HE-06 | 1.8kW 48V LV HE Solar Converter Module |  | 1 | Filled | 1 | 1 | 2021-05-26 | Module not recognised when installed. | SM1848HE-06 |  | No | No Fault Found | 2101010173 | Neal.Peng | 2021-05-27 | First test on bench, turned on by 130Vdc from PSU, Checked good via bench PSU, product ID(??) read correct, 62D2. O/p voltage 54V. See note. | No Fault Found |  |  | Might need Sales Eng to go back to customer first.
RMA0000209 | TLJ Switchgear Ltd. | 2021-05-19 | 1 | RM1524HE-08 | 1.5kW 24V HE Rectifier Module |  | 1 | Filled | 1 | 1 | 2021-05-19 | Damaged prior to shipping. | RM1524HE-08 |  | Yes |  | 2102004062 | Neal.Peng | 2021-05-19 | Out of box failure, unit been dropped prior to shipping. | Damaged Component |  | Rear cornoer of chassis. | BER. Replacement has been sent to customer under C0991. S/N 2102004047
RMA0000207 | Enetek Power Group PTE Ltd | 2021-05-13 | 1 | MRPITEMEE | P-RW624U-21 |  | 1 | Filled | 1 | 0 | 2021-05-19 | Not working | P-RW624U-21 |  | No |  | 1723094800 | Neal.Peng | 2021-05-19 | All FETs and diodes were checked good. Turned it on with AC, only got 24.5V float volage and it's unstable, adjusted trimpot VR205 and o/p voltage jumped to normal value 27.2V See note. | Faulty Component |  | Trimpots | Serviced and ready to go back to customer.
RMA0000206 | Crown Equipment Limited | 2021-05-11 | 1 | MRPITEMMP | FS3LNV-532-NZ01 |  | 1 | Filled | 1 | 0 | 2021-05-19 | Output fuse fault.One after another | FS3LNV-532-NZ01 |  | NA |  | 1332538970 | Jason.Liu | 2021-05-19 | Cannot recreate fault with output fuse. Measured the Fuses and they were in good condition.Unplugged all connections and replugged them back to clean off dust build ups. Unit then put under Resistive Load and Battery Test and passed both. | Environmental & Contamination |  |  | No Fault Found, No Charge, PO# 46507. Invoice to Crown NZ and attention to Craig Graham.
RMA0000204 | DC Power Ltd | 2021-05-11 | 1 | MRPITEMMP | P-BMMU-ECO-00 |  | 1 | Filled | 1 | 1 | 2021-05-13 | The BMM freezes and we can't log in, will say no comms and we can'tcommunicate with the device. | P-BMMU-ECO-00 |  | NA |  | 2005650617
RMA0000203 | Profiler Tech Limited | 2021-05-10 | 1 | MRPITEMCM | Commtest vb7 |  | 1 | Filled | 1 | 0 | 2021-05-17 | Unit makes a high pitched squealing noise but otherwise seems to operate OK. Please check Charger Board specifically. | Commtest vb7 |  | NA |  | 42314 | Eric.Martin | 2021-05-17 | NFF - customer reported that they could hear high pitch sound, but could not recreate issue - changed battery, used different charger. Checked for internal damaged component and found nothing. Re-calibrated. | No Fault Found |  | NA | unit is ready to return to customer
RMA0000201 | Crown Equipment Limited | 2021-05-10 | 1 | MRPITEMMP | FS3LNV-530-NZ01 |  | 1 | Filled | 1 | 0 | 2021-05-10 | Not charge and no display | FS3LNV-530-NZ01 |  | NA |  | 1530791697 | Jason.Liu | 2021-05-11 | MPC failed causing front panel display to be blank and not functional and made modules to turn on in idle state. Replaced with a new one and issues were rectified and unit passed on resistive load and battery test. | Faulty Component |  | Existing MPC - 156780302 (SWEN-MPC35-52)Replaced - 1828279528 (SWEN-MPC35-54) | Return to customer, invoive Crown NZ and attention to Kyle. PO#46415 Service Fee: $214
RMA0000199 | Profiler Tech Limited | 2021-05-03 | 1 | MRPITEMCM | Commtest vb8 |  | 1 | Filled | 1 | 0 | 2021-05-05 | Unit does not power on. | Commtest vb8 |  | NA |  | 41515 | Eric.Martin | 2021-05-05 | replaced faulty Colibri with customer supplied (old) colibri. | Faulty Component |  | Colibri | unit is ready to return to the customer
RMA0000198 | Kordia/FENZ | 2021-05-03 | 1 | PSC24V2-403-001 | 2U +12V/24V, 2R 2C, 11+1L, 3B, EM4x |  | 1 | Filled | 1 | 1 | 2021-05-04 | On start up it goes straight to the Alarm screen. The enter button on the front panel seems to have no function and when exiting to the Enatel Splash screen it immediately jumps to whatever is selected on the Overview screen (default selection is Alarms, hence starting on the alarm screen)S/N of returned Monitor: 2008014656 | PSC24V2-403-001 |  | Yes | NA | 2011005726 | Neal.Peng | 2021-05-04 | Enter button not working. Buttons worked fine on ref unit. Used a ref Linux card on the RMA unit, fault disappear. Tested returned Linux card on ATE and it failed. Looks like IC1 on Linux card got faulty. See note. | Faulty Component |  | IC1 | Serviced and ready to go to customer.
RMA0000197 | Profiler Tech Limited | 2021-05-03 | 1 | MRPITEMCM | Commtest vb8 |  | 1 | Filled | 1 | 0 | 2021-05-05 | Unit will not charge above 51% | Commtest vb8 |  | NA |  | 47047 | Eric.Martin | 2021-05-05 | NFF |  |  | NFF | unit is ready to return to the customer
RMA0000196 | Enetek Power Group PTE Ltd | 2021-04-29 | 1 | MRPITEMEE | P-RM3048HE-08T |  | 1 | Filled | 1 | 1 | 2021-05-11 | No output | P-RM3048HE-08T |  | No | Adverse environment | 1903409808 | Neal.Peng | 2021-05-11 | Unit is very dirty on fan and area behind fan, corrosion could be found on fan, cover, screw, PCB and some parts. Input fuses, boost FETs, primary FETs and secondary FETs were checked good. Fan not working on jig. See note. | Environmental & Contamination |  | Fan, aux circuitry | BER and warranty is voided due to corrosion. Customer confirmed to dispose it at Enatel.
RMA0000195 | Profiler Tech Limited | 2021-04-28 | 1 | MRPITEMCM | Bently Nevada SCOUT140 |  | 1 | Filled | 1 | 0 | 2021-05-05 | Unit loses charge rapidly | Bently Nevada SCOUT140 |  | NA |  | 47082 |  |  | NFF |  |  | NFF | unit is ready
RMA0000194 | Vital Limited | 2021-04-28 | 1 | CM612-48-08 | 600W 12V DC:DC Converter Module |  | 1 | Filled | 1 | 1 | 2021-04-29 | Rectifier LED alarm indications, could not successfully connect monitoring bus to see the exact alarm as the rectifier blew up. Out-of-box failure. | CM612-48-08 |  | Yes | NA | 2010015262 | Neal.Peng | 2021-04-29 | No evidence of blown up, good measurement on all critical parts. Turned unit on with bench supply, found yellow led lit on all the time without any alarm activated. Solder short across P600 and P601. Removed and fault cleared. | Solder Short |  | Yellow LED | Need ES.
RMA0000193 | Vital Limited | 2021-04-28 | 1 | MRPITEMEE | P-SM36-NT2-01 |  | 1 | Filled | 1 | 0 | 2021-05-03 | Fault: Connected single wire bus management on J12 between ultra and 12/24V expansion and the rectifiers blew up | P-SM36-NT2-01 |  | No | No Fault Found | 1902401132 | Neal.Peng | 2021-05-04 | NFF on this monitor. Customer incorrectly connected the rectifiers shelf and the converter shelf, and caused 2x RM2048HEs blew up. | No Fault Found |  |  | Unit is ready to go back to customer.
RMA0000193 | Vital Limited | 2021-04-28 | 2 | MRPITEMEE | P-RM2048HE-12 |  | 1 | Filled | 1 | 0 | 2021-05-03 | Fault: Connected single wire bus management on J12 between ultra and 12/24V expansion and the rectifiers blew up | P-RM2048HE-12 |  | No | Customer electrical damage | 1902395189 | Neal.Peng | 2021-05-04 | Main stage FETs Q115/Q117 failed short, no comms due to PCB fuse for comms burnt out. Root cause suspect incorrect connection by customer shorted the SBI rail and damaged Micro, therefore main stage failed. | Incorrect Customer set-up/operation |  | Q115, Q117, PCB fuse, Micro | Unit is BER and out of warranty. Customer requested it back.
RMA0000193 | Vital Limited | 2021-04-28 | 3 | MRPITEMEE | P-RM2048HE-12 |  | 1 | Filled | 1 | 0 | 2021-05-03 | Fault: Connected single wire bus management on J12 between ultra and 12/24V expansion and the rectifiers blew up | P-RM2048HE-12 |  | No | Customer electrical damage | 1902394760 | Neal.Peng | 2021-05-04 | Main stage FETs Q115/Q117 failed short, no comms due to PCB fuse for comms burnt out. Root cause suspect incorrect connection by customer shorted the SBI rail and damaged Micro, therefore main stage failed. | Incorrect Customer set-up/operation |  | Q115, Q117, PCB fuse, Micro | Unit is BER and out of warranty. Customer requested it back.
RMA0000193 | Vital Limited | 2021-04-28 | 4 | MRPITEMEE | PSC04020160-001 |  | 1 | Filled | 1 | 0 | 2021-05-03 | Fault: Connected single wire bus management on J12 between ultra and 12/24V expansion and the rectifiers blew up | PSC04020160-001 |  | No | No Fault Found | 1903404770 | Neal.Peng | 2021-05-03 | NFF on this shelf. Customer incorrectly connected the rectifiers shelf and the converter shelf, and caused 2x RM2048HEs blew up. | No Fault Found |  |  | Unit is ready to go back to customer.
RMA0000192 | Crown Equipment Limited | 2021-04-28 | 1 | MRPITEMMP | FS3LNV-530-NZ01 |  | 1 | Filled | 1 | 0 | 2021-04-29 | Mains fail, making buzzing noise | FS3LNV-530-NZ01 |  | NA |  | 1742147310 | Jason.Liu | 2021-04-29 | Powered up and unit was buzzing, took off front filter to examine charger modules, all three charger moduels were not locked in place, buzzing noise was made from the loose connection between the backplane connectors and the charger moduels. | UnKnown |  | Re-inserted the three moduels and locked them, tested on Battery and Resistive load and passed on both. | Return to custmer, Charger Service Fee: $214. Please invoice Crown NZ and attention it to Craig Graham.
RMA0000010 | OS Operations, LLC | 2020-08-02 | 1 | MRPITEMCM | 109M2380 |  | 1 | Opened | 1 | 1 |  | EM 20Jul20: Please issue an RMA number and the unit should be returned to us for analysis. Unfortunately the Tach test isn’t automated for the VBX/Scout1XX units.Test AC Path Reading 8Vpp 100 Hz, Ch 2:Failed. Result: 0.001272054036458 VrmsCompare Type: GELE | 109M2380 |  |  | NA | 100766
RMA0000191 | Averge Technologies (Pty) Ptd | 2021-04-27 | 1 | PSC14070561-031 | 5U Compact, -48, 7R, 14kW, Telkom200 | AD500231 | 1 | Filled | 1 | 1 | 2021-05-11 | Received without C/Breaker trip-protect cover. | PSC14070561-031 |  | Yes |  | 2103010254 | Neal.Peng | 2021-04-29 | Missing C/Breaker trip-protect cover. System is not actually returned. We only send the replacement. | Missing Component |  |  | Replacement is ready to go to customer.
RMA0000191 | Averge Technologies (Pty) Ptd | 2021-04-27 | 2 | PSC14070561-031 | 5U Compact, -48, 7R, 14kW, Telkom200 | AD500231 | 1 | Filled | 1 | 1 | 2021-05-11 | Received without C/Breaker trip-protect cover. | PSC14070561-031 |  | Yes |  | 2103010260 | Neal.Peng | 2021-04-29 | Missing C/Breaker trip-protect cover. System is not actually returned. We only send the replacement. | Missing Component |  |  | Replacement is ready to go to customer.
RMA0000191 | Averge Technologies (Pty) Ptd | 2021-04-27 | 3 | PSC14070561-031 | 5U Compact, -48, 7R, 14kW, Telkom200 | AD500231 | 1 | Filled | 1 | 1 | 2021-05-11 | Received without C/Breaker trip-protect cover. | PSC14070561-031 |  | Yes |  | 2103010281 | Neal.Peng | 2021-04-29 | Missing C/Breaker trip-protect cover. System is not actually returned. We only send the replacement. | Missing Component |  |  | Replacement is ready to go to customer.
RMA0000191 | Averge Technologies (Pty) Ptd | 2021-04-27 | 4 | PSC14070561-031 | 5U Compact, -48, 7R, 14kW, Telkom200 | AD500231 | 1 | Filled | 1 | 1 | 2021-05-11 | Received without C/Breaker trip-protect cover. | PSC14070561-031 |  | Yes |  | 2012006863 | Neal.Peng | 2021-04-29 | Missing C/Breaker trip-protect cover. System is not actually returned. We only send the replacement. | Missing Component |  |  | Replacement is ready to go to customer.
RMA0000191 | Averge Technologies (Pty) Ptd | 2021-04-27 | 5 | PSC14070561-031 | 5U Compact, -48, 7R, 14kW, Telkom200 | AD500231 | 1 | Filled | 1 | 1 | 2021-05-11 | Received without C/Breaker trip-protect cover. | PSC14070561-031 |  | Yes |  | 2103010253 | Neal.Peng | 2021-04-29 | Missing C/Breaker trip-protect cover. System is not actually returned. We only send the replacement. | Missing Component |  |  | Replacement is ready to go to customer.
RMA0000191 | Averge Technologies (Pty) Ptd | 2021-04-27 | 6 | PSC14070561-031 | 5U Compact, -48, 7R, 14kW, Telkom200 | AD500231 | 1 | Filled | 1 | 1 | 2021-05-11 | Received without C/Breaker trip-protect cover. | PSC14070561-031 |  | Yes |  | 2012006846 | Neal.Peng | 2021-04-29 | Missing C/Breaker trip-protect cover. System is not actually returned. We only send the replacement. | Missing Component |  |  | Replacement is ready to go to customer.
RMA0000191 | Averge Technologies (Pty) Ptd | 2021-04-27 | 7 | PSC14070561-031 | 5U Compact, -48, 7R, 14kW, Telkom200 | AD500231 | 1 | Filled | 1 | 1 | 2021-05-11 | Received without back plain cover. | PSC14070561-031 |  | Yes |  | 2103010247 | Neal.Peng | 2021-04-29 | Missing back plain cover. System is not actually returned. We only send the replacement. | Missing Component |  |  | Replacement is ready to go to customer.
RMA0000191 | Averge Technologies (Pty) Ptd | 2021-04-27 | 8 | PSC14070561-031 | 5U Compact, -48, 7R, 14kW, Telkom200 | AD500231 | 1 | Filled | 1 | 1 | 2021-05-11 | Received without back plain cover. | PSC14070561-031 |  | Yes |  | 2103010269 | Neal.Peng | 2021-04-29 | Missing back plain cover. System is not actually returned. We only send the replacement. | Missing Component |  |  | Replacement is ready to go to customer.
RMA0000191 | Averge Technologies (Pty) Ptd | 2021-04-27 | 9 | PSC14070561-031 | 5U Compact, -48, 7R, 14kW, Telkom200 | AD500231 | 1 | Filled | 1 | 1 | 2021-05-11 | Received without back plain cover. | PSC14070561-031 |  | Yes |  | 2103010256 | Neal.Peng | 2021-04-29 | Missing back plain cover. System is not actually returned. We only send the replacement. | Missing Component |  |  | Replacement is ready to go to customer.
RMA0000190 | Vital Limited | 2021-04-22 | 1 | MRPITEMEE | P-RM2048HE-12 |  | 1 | Filled | 1 | 0 | 2021-04-27 | Fault: equipment was removed from service due to failure incurred during Ambulance network upgrade. | P-RM2048HE-12 |  | No | Customer electrical damage | 1837311332 | Neal.Peng | 2021-04-27 | '-DC output pins burnt/melted. Opened unit and found couple of died flies. Input fuses open, half main stage FETs failed short, half secondary stage FETs failed short, Q309A blown up.See note. | Incorrect Customer set-up/operation |  | Q309/Q309A, Q311/Q311A, Q115, Q117, FH101, FH102, PCB fuse | BER due to damaged PCB. Warranty is voided. Customer confirmed units can be scrapped here.
RMA0000190 | Vital Limited | 2021-04-22 | 2 | MRPITEMEE | P-RM2048HE-12 |  | 1 | Filled | 1 | 0 | 2021-04-27 | Fault: equipment was removed from service due to failure incurred during Ambulance network upgrade. | P-RM2048HE-12 |  | No | Customer electrical damage | 1837311200 | Neal.Peng | 2021-04-27 | Input fuses opened, half main stage FETs failed short. No comms when backfeeding. PCB fuse under J301 used for comms burnt, this shows symptom that the customer might reverse polarity while connecting. See note. | Incorrect Customer set-up/operation |  | PCB fuse, FH101, FH102, Q115, Q117 | BER due to damaged PCB. Warranty is voided. Customer confirmed units can be scrapped here.
RMA0000188 | Enetek Power Group PTE Ltd | 2021-04-21 | 1 | MRPITEMEE | P-RM3048HE-08T |  | 1 | Filled | 1 | 1 | 2021-05-11 | module fan failsystem installed at rooftop, under the IP66 rated cabinet | P-RM3048HE-08T |  | No | Adverse environment | 1904437194 | Neal.Peng | 2021-05-11 | Dusty on fan and area behand fan. Input fuses, boost FETs, primary FETs and secondary FETs were check good. Aux rails and w/fs checked good on bench. Got short circuit when tested fan on jig, fan died. New fan worked good on unit. See note. | Environmental & Contamination |  | Fan | Serviced and ready to go back to customer.
RMA0000185 | Indochina Technology JSC | 2021-04-19 | 1 | RM2048XE-38 | 2kW 48V Rectifier Module |  | 1 | Filled | 1 | 1 | 2021-04-29 | Fan fail anh faulty | RM2048XE-38 |  | Yes |  | 2009008088 | Neal.Peng | 2021-05-03 | Input fuses, diode bridge, boost FETs and main FETs were checked good. R634/R634A burnt out. Fan not worked on jig. Considering its age, suspect root cause is unknown voltage swell on secondary aux rail killed fan and fan drive. | Damaged Component |  | Q195 Fan R634 R634A | Unit has been serviced and ready to go to customer.
RMA0000185 | Indochina Technology JSC | 2021-04-19 | 2 | RM2048XE-38 | 2kW 48V Rectifier Module |  | 1 | Filled | 1 | 1 | 2021-04-29 | Fan fail anh faulty | RM2048XE-38 |  | Yes |  | 2008018372 | Neal.Peng | 2021-05-03 | Input shunts blew up, all main stage FETs failed, R634/R634A burnt out, fan not ran on jig. Pad got damaged due to blown up. See note. | Damaged Component |  | Q195 Fan R634 R634A Q184 Q185 Q186 Q187 R21A R22A | Unit is BER due to damaged PCB, in warranty. Need replacement to be sent to customer.
RMA0000185 | Indochina Technology JSC | 2021-04-19 | 3 | RM2048XE-38 | 2kW 48V Rectifier Module |  | 1 | Filled | 1 | 1 | 2021-04-29 | Fan fail anh faulty | RM2048XE-38 |  | Yes |  | 2008018137 | Neal.Peng | 2021-05-03 | Input fuses, diode bridge, boost FETs and main FETs were checked good. R634/R634A burnt out. Fan not worked on jig. Considering its age, suspect root cause is unknown voltage swell on secondary aux rail killed fan and fan drive. | Damaged Component |  | Q195 Fan R634 R634A | Unit has been serviced and ready to go to customer.
RMA0000184 | CPS National Pty Ltd - Attn: Greg Campbell | 2021-04-19 | 1 | MEC-SHC1U400-06 | 1U 4 Across 1kW DC/DC Shelf V6 |  | 1 | Filled | 1 | 1 | 2021-05-10 | Converter in Vodafone Trial site went faulty. Swapped it to other positions but this made no difference. Murray Wyma is across the issue.All 3 modules failed and would be returned. | MEC-SHC1U400-06 |  | NA |  | 2006671190 | Neal.Peng | 2021-05-11 | Passed System test, done by Eric Chen.
RMA0000184 | CPS National Pty Ltd - Attn: Greg Campbell | 2021-04-19 | 2 | CM1860-48-15 | DC-DC converter 1.8KW 60/48 |  | 1 | Filled | 1 | 1 | 2021-05-10 | Converter in Vodafone Trial site went faulty. Swapped it to other positions but this made no difference. Murray Wyma is across the issue. | CM1860-48-15 |  | NA |  | 2008017214 | Neal.Peng | 2021-05-11 | Vop58.08V, Vnoise30mV@25A, IL31A, OVSD59.9V. Current hold at 32.6A. Passed BI.
RMA0000184 | CPS National Pty Ltd - Attn: Greg Campbell | 2021-04-19 | 3 | CM1860-48-15 | DC-DC converter 1.8KW 60/48 |  | 1 | Filled | 1 | 1 | 2021-05-10 | Converter in Vodafone Trial site went faulty. Swapped it to other positions but this made no difference. Murray Wyma is across the issue.All 3 modules failed and would be returned. | CM1860-48-15 |  | NA |  | 2008017250 | Neal.Peng | 2021-05-11 | Vop56.8V, Vnoise25mV@25A, IL31A, OVSD59.8V. Current hold at 33.6A. Passed BI.
RMA0000184 | CPS National Pty Ltd - Attn: Greg Campbell | 2021-04-19 | 4 | CM1860-48-15 | DC-DC converter 1.8KW 60/48 |  | 1 | Filled | 1 | 1 | 2021-05-10 | Converter in Vodafone Trial site went faulty. Swapped it to other positions but this made no difference. Murray Wyma is across the issue.All 3 modules failed and would be returned. | CM1860-48-15 |  | NA |  | 2008017238 | Neal.Peng | 2021-05-11 | Vop58.01V, Vnoise25mV@25A, IL30.2A, OVSD59.9V. Current hold at 32.7A. Passed BI.
Finished RMAs in May
RMA No | Quantity of investigated items | Quantity of serviced items | Quantity of BER
RMA0000213 | 1 | 0 | 1
RMA0000206 | 1 | 1 | 0
RMA0000201 | 1 | 1 | 0
RMA0000192 | 1 | 1 | 0
Grand Total | 4 | 3 | 1
Warranty
RMA No | In warratny quantity | Out of warranty quantity | Warranty void
RMA0000213 | 0 | 1 | 0
RMA0000206 | 0 | 1 | 0
RMA0000201 | 0 | 1 | 0
RMA0000192 | 0 | 1 | 0
Grand Total | 0 | 4 | 0